ALICE Work Package Document                                                         	CERN  					EDMS No: 551035

CH-1211 GENEVE 23				ALI-SER-SPC-0027, v.5

Switzerland

Date of last change: 6/7/2006

Work Package Document for

ALICE Electrical Distribution Systems

J.M. Bernal (TS-EL) and J.P. Vanuxem (PH-AIS)

# Abstract

This Work Package Document outlines the sharing of responsibilities between the ALICE Collaboration and CERN TS-EL with respect to the design, construction, installation, operation and maintenance of Electrical Distribution Systems for the ALICE experiment itself, general services at point 2 and power and control for the two magnets excluded. It summarizes the material requirements and the costs for the implied Work Units.

Table of Contents

Abstract	1

Introduction	3

Work Units	3

General	3

Work Unit 1, Primary Electrical Distribution of Standard Power	4

Short description:	4

Tasks included in this work unit:	4

Responsibilities:	4

Agreed resources:	5

Work Unit 2, Secondary Electrical Distribution of Standard Power	6

Short description:	6

Tasks included in this work unit:	7

Responsibilities:	7

Agreed resources:	7

Work Unit 3, Electrical Distribution of UPS Power	8

Short description:	8

Tasks included in this work unit:	10

Responsibilities:	11

Agreed resources:	11

Appendices	12

General information	12

Appendix A: Distribution of Standard Power in UX25	13

Appendix B: Distribution of Standard Power in PX24 and SX2	17

Appendix C: Distribution of Power to Cooling Units	22

Appendix D: Distribution of UPS power in ALICE	23

# Introduction

This document defines the responsibilities for the Design, Manufacture, Installation and Testing of the ALICE Electrical Distribution Systems. It details the help that is expected from the CERN TS-EL and PH-AIS (ALICE Integration Team) groups. The package is divided into work units which define the responsibilities for each system. The overall responsibility for this Work Package lies with the ALICE Integration Team.

# Work Units

## General

Listed below are the work units associated with this work package:

|  | Description | Responsible | Division/Group |
| --- | --- | --- | --- |
| Work package | ALICE Electrical Distribution Systems | J.P. Vanuxem | PH-AIS |

| Work Unit | Description | Responsible | Division/Group |
| --- | --- | --- | --- |
| Work Unit 1 | Primary Electrical Distribution of Standard Power | J.M. Bernal | TS-EL |
| Work Unit 2 | Secondary Electrical Distribution of Standard Power | J.M. Bernal | TS-EL |
| Work Unit 3 | Distribution of UPS Power | J.M. Bernal | TS-EL |

Each work unit will consist of various items of equipment, both hardware and software, which are attributed to the responsible group for the design, procurement, assembly, installation and testing.

## Work Unit 1, Primary Electrical Distribution of Standard Power

### Short description:

Covers the triple-phase, 400V primary electrical distribution of standard power in the surface building (SX2), the access shaft (PX24) and the underground experimental area (UX25) at Point 2, and includes the following items:

### Tasks included in this work unit:

- Cabling the connections between the primary distribution unit (PDU) EXD1/2X fed by a 18kV/400V, 2 MVA transformer in SX2 and 6 secondary distribution units (SDU). Five of these SDU’s are of the standard “Hazemeyer” type: 4 double units (Haz-D) for the four counting rooms CR1 to CR4 of PX24 shaft, and 1 single unit (Haz-S) for the plug platform CR5  of  PX24 shaft. The 6th SDU is a ‘Prisma’ wall switchboard and feeds racks in the Alice Control Room (ACR) situated in surface building SX25.

- Cabling the connections between the primary distribution unit EXD1/25 fed by a 18kV/400V, 1.25 MVA transformer in US25 and 7 secondary distribution units of standard “Hazemeyer” type (all Haz-D) in experimental cavern UX25.

- Cabling the connections between the primary distribution unit EQD1/25 fed by a 18kV/400V, 1.25 MVA transformer in US25 and a special, “TS-CV1” secondary distribution unit for detector cooling equipment in experimental cavern UX25.

- TS-EL control and monitoring of contactors / circuit breakers + monitoring of voltages / currents of all three PDU’s.

- Link to DCS control and monitoring system.

- Control and supervision software.

- Test and commissioning.

- Maintenance and operation.

### Responsibilities:

Technical coordination 	ALICE Integration Team

Project leader			J.M. Bernal, TS-EL

### Agreed resources:

|  | Number | Estimated Cost (kCHF) | Budget Code |
| --- | --- | --- | --- |
| Primary Distribution Units (PDU) EXD 1/2X, EXD1/25 and EQD1/25 | 3 | 0 (L3) | NA |
| Cabling from Transfo 1 (2 MVA) to EXD1/2X in SX2 | 1 | 0 (L3) | NA |
| Cabling from Transfo 2 (1.25 MVA) to EXD1/25 in US25 | 1 | 0 (L3) | NA |
| Cabling from Transfo 3 (1.25 MVA) to EQD1/25 in US25 | 1 | ? | ? |
| Secondary Distribution Units (SDU) in SX2 and PX24 | 4 Haz-D 1 Haz-S 1 ‘Prisma’ | 0 (L3) 0 (L3) ? | NA |
| Cabling from EXD1/2X to the 6 SDU’s in SX2 and PX24 | 4 + 1 +1 | ? | ? |
| Secondary Distribution Units (SDU) in UX25 | 7 Haz-D | 0 (L3) | NA |
| Cabling from EXD1/25 to the 7 SDU’s in UX25 | 7 | ? | ? |
| Secondary Distribution Unit (SDU) of special TS-CV1 type for detector cooling units in UX25 | 1 | ? | ? |
| Cabling from EQD1/25 to TS-CV1 in UX25 | 1 | ? | ? |
| TS-EL Control and Monitoring of all 3 PDU’s (hardware + software) | NA | ? | ? |

## Work Unit 2, Secondary Electrical Distribution of Standard Power

### Short description:

Covers the triple-phase, 400V secondary electrical distribution of standard power between:

1) 5 secondary distribution units (SDU) of the standard Hazemeyer type (4 double ‘Haz-D’ and 1 single ‘Haz-S’) and the 116 (+9 spare) racks in PX24:

-    114 racks (+9 spare) in the four counting rooms CR1-CR4

-    2 racks on the CR5 platform (i.e. the ‘plug’)

2) 7 secondary distribution units of the standard Hazemeyer type (all Haz-D) and 111 (+23 spare) racks in UX25.

3) 1 ‘Prisma’ wall switchboard and 1 rack in SX2 (ACR)

4) 1 special ‘TS-CV1’ secondary distribution unit and 8 cooling units in the A area of UX25 cavern.

The following table summarized the secondary electrical distribution of standard power to electronic racks and cooling units in ALICE, with its 14 SDU’s (mostly Hazemeyer units).

| Area | in CR/ Group | SDU type | SDU name | Racks connected | # of Racks (+ spare) | HM Connexion mode |
| --- | --- | --- | --- | --- | --- | --- |
| PX24 | CR1 | Haz-D | EXD1/20 | X01-X11, Y01-Y14, Z01, Z09-Z10 | 28 (+0) | 1 HM for 2 racks |
| PX24 | CR2 | Haz-D | EXD2/20 | X01-X10, Y05-Y17, Z01-Z13 | 36 (+0) | 1 HM for 2 racks |
| PX24 | CR3 | Haz-D | EXD3/20 | X01-X12, Y01-Y08 | 20 (+7) | 1 HM for 2 racks |
| PX24 | CR4 | Haz-D | EXD4/20 | X01-X09, Y01-Y14, Z01-Z07 | 30 (+2) | 1 HM for 2 racks |
| PX24 | CR5 | Haz-S | EXD5/20 | X07-X08 | 2 (+0) | 1 HM for 2 racks |
| UX25 | I | Haz-D Haz-D | EXD6/29 EXD7/29 | I16, I08-I00 I37-I17 | 10 (+7) 21 (+0) | 1 HM per rack 1 HM per rack |
| UX25 | O | Haz-D Haz-D | EXD4/29 EXD5/29 | O16-O12, O08-O02 O37-O23, O19-O18 | 12 (+5) 17 (+0) | 1 HM per rack 1 HM per rack |
| UX25 | A | Haz-D | EXD1/29 | A03-A09, A12-A21 | 17 (+5) | 1 HM per rack |
| UX25 | C | Haz-D Haz-D | EXD2/29 EXD3/29 | C00-C05, C08-C11, C12-C18, C20-C21 C22-C32, C36-C39 | 19 (+3) 15 (+3) | 1 HM per rack 1 HM per rack |
| SX2 | ACR | Prisma | EBD8/2X | X01 | 1 (+0) | 1 HM per rack |
| UX25 | A | Special | TS-CV1 (Std power) | TS-CV cooling units (CU) | 8 CU | One 3-phase feeder per CU |

The details of the secondary distribution of standard power in PX24 and SX2 are given in Appendix A and Appendix B respectively.

The secondary distribution of UPS power is described separately in the following chapter.

The two special secondary distribution units (TS-CV1  for standard power and TS-CV2 for UPS power) and their connection to TS/CV cooling units are  detailed in Appendix C.

### Tasks included in this work unit:

- Updating, retesting, installing and cabling all standard secondary distribution units (Hazemeyer) to end user electronic racks.

- Cabling the special TS-CV1 distribution unit to 8 detector cooling units.

- TS-EL Control and monitoring of contactors / circuit breakers + monitoring of voltages / currents of all SDU’s.

- Link to DCS Control and monitoring system.

- Control and supervision software.

- All tests and commissioning.

- Maintenance and operation.

### Responsibilities:

Technical coordination 	ALICE Integration Team

Project leader			J.M. Bernal, TS-EL

### Agreed resources:

|  | Number | Estimated Cost | Budget Code |
| --- | --- | --- | --- |
| Cabling from 5 “Hazemeyer” SDU’s (4 Haz-D + 1 Haz-S) to electronic racks in CR1-CR5 | 116 | ? | ? |
| Cabling from 7 “Hazemeyer” SDU’s (all Haz-D) to electronic racks in UX25 | 111 | ? | ? |
| Cabling from 1 “Prisma” to one rack in ACR | 1 | ? | ? |
| Cabling from 1 special “TS-CV1” SDU to 8 detector cooling units in UX25 | 8 | ? | ? |
| TS-EL Control and Monitoring of all 14 SDU’s (hardware + software) | NA | ? | ? |

## Work Unit 3, Electrical Distribution of UPS Power

### Short description:

Covers the production of triple-phase, 400 V Uninterruptable Power Supply (UPS) and its distribution to some 30 racks and 8 cooling units in ALICE. It is necessary in ALICE for safety reasons (staff and/or equipment). An eventual lack of power upstream is immediately compensated by a UPS unit which takes its own power from internal batteries (autonomy time of batteries  5-10 min).

CERN Safety Instruction note IS40 should be followed for the implementation of UPS at point 2.

The figure below shows the two different protection levels of UPS power provided in ALICE by three physical UPS units.

DIESEL

EDF

UPS1

(ESS 307/2X)

EOS

EDF

UPS2

(EBS 106/2X)

EOS

GES

GES

Auto-transfer

within 10 s

Diesel provides full power within 30 s

Auto-transfer

within 10 s

EOD1/20

EOD3/2X

EOD1/2X

UPS3

(EBS 128/2X)

Level 2 (60 kVA)

Level 1 (20kVA)

Level 2 (80 kVA)

The two different protection levels in ALICE are further detailed below, following an ascending level of protection:

Level 2 power is required to protect essential parts of the experiment from power cuts, and eventually also from surges on the mains. It is provided by two existing UPS units (80 kVA by UPS2 and 60 kVA by UPS3). UPS2 is already connected to the EDF-EOS CERN “auto-transfer” network, while UPS3 needs to be connected to the same network. About 10 seconds are required for the switching from EDF to EOS to take place in case of a power cut on the EDF network, but the load remains powered during switching time via the internal batteries of the UPS unit. This UPS power is cut by the general emergency stop (GES), more commonly known as ’Arrêt d’Urgence Général’ (AUG).

Level 1 power (the ultimate in safety!) is a diesel backed-up UPS power. It is mostly aimed at protecting people by delivering sustained power to lifts, fume evacuation units, minimum (anti-panic) lighting systems, etc… during a long power cut on the mains. The diesel needs about 30 seconds to start after a power cut has been detected on both EDF and EOS networks, but the load remains powered during start up time via the internal batteries of the UPS unit. Its use in ALICE for protecting vital parts of the experiment is limited to 20 kVA, provided by UPS1 unit. This UPS power is not cut by the general emergency stop.

UPS power will be used by ALICE  as shown in the following table. Total UPS power available (the line before last of the table) is given in kW after reduction of the kVA figures (last line of the table) by a typical power factor of 0.8.  In the same table are detailed for each system concerned the connected racks and the SDU name as used by the TS-EL nomenclature.

| System | Connected Racks | SDU name (location) | Level 1 UPS1 (kW) | Level 2 UPS2 (kW) | Level 2 UPS3 (kW) | All UPS (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| DSS | CR4-Z09 | EOD3/2X (SX2) | 1 |  |  | 1 |
| DSS in ACR | SX2-X01 | EOD3/2X (SX2) | 1 |  |  | 1 |
| TPC-VHV | CR4-Z08 | EOD3/2X (SX2) | 1 |  |  |  |
| MSS + MCS | 2 racks in MCR | EOD3/2X (SX2) | 6.2 |  |  | 6.2 |
| Sniffer Control | CR5-X01 | EOD3/2X (SX2) | 0.9 |  |  | 0.9 |
| Sniffer Detection | O23-O21 | EOD3/2X (SX2) | 4.8 |  |  | 4.8 |
| Ethernet Starpoint | CR2 level, staircase South | EOD3/2X (SX2) | 1 |  |  | 1 |
| DCS | CR3-(Z01-Z08) | EOD1/20 (CR4) |  | 47.6 |  | 47.6 |
| HLT | CR2-(Y01-Y04) | EOD1/20 (CR4) |  | 5 |  | 5 |
| DAQ | CR1-(Z02-Z08) | EOD1/2X (SX2) |  |  | 27 | 27 |
| Fire Detection | CR5-(X02-X04) | EOD1/2X (SX2) |  |  | 6.9 | 6.9 |
| Radio-protection | CR5-X05 | EOD1/2X (SX2) |  |  | 0.4 | 0.4 |
| Under-pressure Cooling Systems | TS-CV2 in A | EOD1/2X (SX2) |  |  | 6.4 | 6.4 |
| Total UPS consumption in kW |  |  | 15.9 | 52.6 | 40.7 | 110.2 |
| Total UPS available in kW |  |  | 16kW | 64kW | 48kW | 128kW |
| Total UPS available in kVA |  |  | 20kVA | 80kVA | 60kVA | 160kVA |

The details of the distribution of UPS power in ALICE are given in Appendix D.

### Tasks included in this work unit:

- Cabling UPS1 to diesel backed-up network and to EOD3/2X (dotted line).

- Cabling UPS3 to auto-transfer network (dotted line).

- Updating, retesting and cabling the 3 standard secondary distribution units (Hazemeyer) EOD1/20 (in CR4), EOD1/2X and EOD3/2X (both in SX2) to end user electronic racks (dotted lines).

- TS-EL Control and monitoring of contactors / circuit breakers + monitoring of voltages / currents of all SDU’s.

- Link to DCS Control and monitoring system.

- Control and supervision software.

- All tests and commissioning.

- Maintenance and operation.

### Responsibilities:

Technical coordination 	ALICE Integration Team

Project leader			J.M. Bernal, TS-EL

### Agreed resources:

|  | Number | Estimated Cost (kCHF) | Budget Code |
| --- | --- | --- | --- |
| UPS1 (20 kVA), new | 1 | 11 | NA |
| UPS2 (80 kVA), existing (MGE type) updated | 1 | 20 | NA |
| UPS3 (60 kVA), existing (MGE type) | 1 | NA | NA |
| Update and retest of 3 SDU’s: EOD2/2X, EOD1/20 and EOD1/2X | 3 |  |  |
| Cabling of UPS1 (20 kVA) to diesel backed up network and to EOD3/2X in SX2 | 1 | ? | ? |
| Cabling of UPS2 (80 kVA) to auto-transfer network and to EOD1/20 in CR4 (already existing) | 1 | NA | NA |
| Cabling of UPS3 (60 kVA) to auto-transfer network and to EOD1/2X in SX2 | 1 | ? | ? |
| Cabling EOD3/2X to end user racks (CR4, CR5, MCR, SX2, UX25) | 9 | ? | ? |
| Cabling EOD1/20 to end user racks (CR2, CR3) | 12 | ? | ? |
| Cabling EOD1/2X to end user racks (CR1, CR5) and TS-CV2 (UX25) | 13 | ? | ? |
| TS-EL Control and Monitoring of all 3 UPS units and 3 SDU’s (hardware + software) | NA | ? | ? |

# Appendices

## General information

The following remarks apply to the tables in the appendices.

1) A Hazemeyer secondary distribution unit provides a maximum of either 9 departures (‘single’ Hazemeyer Haz-S), or 22 departures (‘double’ Hazemeyer Haz-D).  All Hazemeyer departures feeding racks are 3-phase/400V and can normally supply 32A on all 3 phases with a maximum total power of 18 kW/rack, except those feeding ‘high power racks’ with 63A on all 3 phases with a maximum total power of 35 kW/rack. There are in ALICE altogether 9 high power racks which are clearly differentiated by their names being flanked by 2 arrows in p. 13-14 ; (example: ▲I29▲).

2) The phase (R,S, or T) on which the single-phase, 220V power is taken by the end user is chosen at the level of the internal rack power distribution unit ( mostly ‘Normabarre’  for LEP-type racks in CR1-CR5, or a special distribution box placed at the top rear side of rack for LHC-type racks in UX25 cavern ) in such a way as to obtain an even overall phase distribution, the only guarantee for a low-noise, well-balanced electrical distribution system in ALICE.

3) 9 racks are dedicated to the control of the electrical distribution system:

CR1-X01, CR2-X01, CR3-Y01, CR4-Z01, I16, I17, O16, A18 and C00. They are fed with 3-phase 400 V AC power like any other rack, but they also receive 48 V DC power from a special network (EDB), not represented here. These racks are differentiated from normal user racks by means of an asterisk in appendices A and B (example: I16*).

4) Due to the restricted number of existing available Hazemeyer Modules (HM) which have been inherited from LEP times, each Hazemeyer departure (one per ZTBX32 ‘drawer’) feeds 2 racks in the 4 counting rooms CR1-CR4, at least for ‘standard’ (i.e. non UPS) power. Elsewhere, it normally feeds a single rack.

5) There are some unused HM departures. Other departures are not connected, but they are reserved for, either an empty spare rack location, or an unequipped existing spare rack, or an existing spare rack with just its power cable already drawn (but not connected), or an existing spare rack with just their power cable drawn and connected to an internal distribution unit (‘Normabarre’ or power distribution box), or a minimally-equipped spare rack, or a fully-equipped allocated  (either used or spare) rack . The following summary indicates the symbol used in the ‘Spare Status’ column for each case:

| Designation | Spare Status | Rack | Power Cable | Power Distribution | Ventilation and Cooling | Example |
| --- | --- | --- | --- | --- | --- | --- |
| Unused HM Departure | unused | NO | NO | NO | NO | (EXD 723/29) |
| Spare Rack Location | SRL | NO | NO | NO | NO | (EXD 608/29) |
| Spare Rack: Unequipped | SRU | YES | NO | NO | NO | (EXD 407/29) |
| Spare Rack: Cable only | SRC | YES | YES | NO | NO | EXD 311/20 |
| Spare Rack: Minimally equipped | SRM | YES | YES | YES | NO | EXD 312/20 |
| Allocated, fully equipped rack (used or spare) |  | YES | YES | YES | YES | EXD 702/29 |

## Appendix A: Distribution of Standard Power in UX25

Group ‘I’

EXD7/29 (Haz-D)		                  		EXD6/29 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD702/29 | I37 |  | 1 | EXD602/29 | I16*, I17* |  |
| 2 | EXD703/29 | I36 |  | 2 | (EXD603/29) | (I15) | SRL |
| 3 | EXD704/29 | I35 |  | 3 | (EXD604/29) | (I14) | SRL |
| 4 | EXD705/29 | I34 |  | 4 | (EXD605/29) | (I13) | SRL |
| 5 | EXD706/29 | I33 |  | 5 | (EXD606/29) | (I12) | SRL |
| 6 | EXD707/29 | I32 |  | 6 | (EXD607/29) | (I11) | SRL |
| 7 | EXD708/29 | I31 |  | 7 | (EXD608/29) | (I10) | SRL |
| 8 | EXD709/29 | I30 |  | 8 | (EXD609/29) | (I09) | SRL |
| 9 | EXD710/29 | ▲I29▲ |  | 9 | EXD610/29 | I08 |  |
| 10 | EXD711/29 | ▲I28▲ |  | 10 | EXD611/29 | I07 |  |
| 11 | EXD712/29 | ▲I27▲ |  | 11 | EXD612/29 | ▲I06▲ |  |
| 12 | EXD713/29 | ▲I26▲ |  | 12 | EXD613/29 | I05 |  |
| 13 | EXD714/29 | I25 |  | 13 | EXD614/29 | I04 |  |
| 14 | EXD715/29 | I24 |  | 14 | EXD615/29 | I03 |  |
| 15 | EXD716/29 | I23 |  | 15 | EXD616/29 | I02 |  |
| 16 | EXD717/29 | I22 |  | 16 | EXD617/29 | I01 |  |
| 17 | EXD718/29 | I21 |  | 17 | EXD618/29 | I00 |  |
| 18 | EXD719/29 | I20 |  | 18 | (EXD619/29) | --- | unused |
| 19 | EXD720/29 | I19 |  | 19 | (EXD620/29) | --- | unused |
| 20 | EXD721/29 | I18 |  | 20 | (EXD621/29) | --- | unused |
| 21 | (EXD722/29) | --- | unused | 21 | (EXD622/29) | --- | unused |
| 22 | (EXD723/29) | --- | unused | 22 | (EXD623/29) | --- | unused |

Group ‘O’

EXD5/29 (Haz-D)			  		 EXD4/29 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD502/29 | O37 |  | 1 | EXD402/29 | O16* |  |
| 2 | EXD503/29 | O36 |  | 2 | EXD403/29 | O15 |  |
| 3 | EXD504/29 | O35 |  | 3 | EXD404/29 | O14 |  |
| 4 | EXD505/29 | O34 |  | 4 | EXD405/29 | O13 |  |
| 5 | EXD506/29 | O33 |  | 5 | EXD406/29 | O12 |  |
| 6 | EXD507/29 | O32 |  | 6 | (EXD407/29) | (O11) | SRL |
| 7 | EXD508/29 | O31 |  | 7 | (EXD408/29) | (O10) | SRL |
| 8 | EXD509/29 | O30 |  | 8 | (EXD409/29) | (O09) | SRL |
| 9 | EXD510/29 | O29 |  | 9 | EXD410/29 | O08 |  |
| 10 | EXD511/29 | ▲O26▲ |  | 10 | EXD411/29 | O07 |  |
| 11 | EXD512/29 | ▲O27▲ |  | 11 | EXD412/29 | ▲O06▲ |  |
| 12 | EXD513/29 | ▲O28▲ |  | 12 | EXD413/29 | O05 |  |
| 13 | EXD514/29 | O25 |  | 13 | EXD414/29 | O04 |  |
| 14 | EXD515/29 | O24 |  | 14 | EXD415/29 | O03 |  |
| 15 | (EXD516/29) | --- | unused | 15 | EXD416/29 | O02 |  |
| 16 | (EXD517/29) | --- | unused | 16 | (EXD417/29) | (O01) | SRL |
| 17 | (EXD518/29) | --- | unused | 17 | (EXD418/29) | (O00) | SRL |
| 18 | EXD519/29 | O20 |  | 18 | (EXD419/29) | --- | unused |
| 19 | EXD520/29 | O19 |  | 19 | (EXD420/29) | --- | unused |
| 20 | EXD521/29 | O18 |  | 20 | (EXD421/29) | --- | unused |
| 21 | (EXD522/29) | --- | unused | 21 | (EXD422/29) | --- | unused |
| 22 | (EXD523/29) | --- | unused | 22 | (EXD423/29) | --- | unused |

Group ‘A’

EXD1/29 (Haz-D)

| # | HM # | Rack | Spare Status |
| --- | --- | --- | --- |
| 1 | (EXD102/29) | (A00) | SRL |
| 2 | EXD103/29 | A18* |  |
| 3 | EXD104/29 | A19 |  |
| 4 | EXD105/29 | A04 |  |
| 5 | EXD106/29 | A05 |  |
| 6 | EXD107/29 | A06 |  |
| 7 | EXD108/29 | A07 |  |
| 8 | EXD109/29 | A08 |  |
| 9 | EXD110/29 | A09 |  |
| 10 | EXD111/29 | A03 |  |
| 11 | (EXD112/29) | (A10) | SRL |
| 12 | EXD113/29 | A12 |  |
| 13 | (EXD114/29) | (A11) | SRL |
| 14 | EXD115/29 | A14 |  |
| 15 | (EXD116/29) | (A01) | SRL |
| 16 | EXD117/29 | A16 |  |
| 17 | EXD118/29 | A17 |  |
| 18 | (EXD119/29) | (A02) | SRL |
| 19 | EXD124/29 | A15 |  |
| 20 | EXD121/29 | A20 |  |
| 21 | EXD122/29 | A21 |  |
| 22 | EXD123/29 | A13 |  |

Group ‘C’

EXD2/29 (Haz-D)			  	 EXD3/29 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD202/29 | C01 |  | 1 | EXD302/29 | C23 |  |
| 2 | EXD203/29 | C00* |  | 2 | EXD303/29 | C24 |  |
| 3 | EXD204/29 | C03 |  | 3 | EXD304/29 | C25 |  |
| 4 | EXD205/29 | C04 |  | 4 | EXD305/29 | C26 |  |
| 5 | EXD206/29 | C05 |  | 5 | EXD306/29 | C27 |  |
| 6 | EXD207/29 | C02 |  | 6 | EXD307/29 | C28 |  |
| 7 | EXD208/29 | C13 | SRM | 7 | EXD308/29 | C29 |  |
| 8 | EXD209/29 | C08 |  | 8 | EXD309/29 | C30 |  |
| 9 | EXD210/29 | C09 |  | 9 | EXD310/29 | C31 |  |
| 10 | EXD211/29 | C10 |  | 10 | EXD311/29 | C32 |  |
| 11 | EXD212/29 | C11 |  | 11 | (EXD312/29) | (C33) | SRL |
| 12 | EXD213/29 | C12 | SRM | 12 | EXD313/29 | C38 |  |
| 13 | EXD214/29 | C14 |  | 13 | EXD314/29 | C39 |  |
| 14 | (EXD215/29) | (C07) | SRL | 14 | EXD315/29 | C36 |  |
| 15 | EXD216/29 | C15 |  | 15 | EXD316/29 | C37 |  |
| 16 | EXD217/29 | C16 |  | 16 | (EXD317/29) | (C34) | SRL |
| 17 | EXD218/29 | C17 |  | 17 | (EXD318/29) | (C35) | SRL |
| 18 | EXD219/29 | C18 |  | 18 | (EXD319/29) | --- | unused |
| 19 | EXD220/29 | C19 | SRC | 19 | (EXD320/29) | --- | unused |
| 20 | EXD221/29 | C20 |  | 20 | (EXD321/29) | --- | unused |
| 21 | EXD222/29 | C21 |  | 21 | (EXD322/29) | --- | unused |
| 22 | EXD223/29 | C22 |  | 22 | (EXD323/29) | --- | unused |

## Appendix B: Distribution of Standard Power in PX24 and SX2

EXD1/20 in CR1 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD102/20 | CR1-X01* CR1-X02 |  | 12 | (EXD113/20) | --- | unused |
| 2 | (EXD103/20) | --- | unused | 13 | EXD114/20 | CR1-Y01 CR1-Y02 |  |
| 3 | EXD104/20 | CR1-X03 CR1-X04 |  | 14 | EXD115/20 | CR1-Y09 CR1-Y10 |  |
| 4 | EXD105/20 | CR1-Z01 |  | 15 | EXD116/20 | CR1-Y03 CR1-Y04 |  |
| 5 | EXD106/20 | CR1-X05 CR1-X06 |  | 16 | EXD117/20 | CR1-Y07 CR1-Y08 |  |
| 6 | EXD107/20 | CR1-Y13 CR1-Y14 |  | 17 | EXD118/20 | CR1-Y05 CR1-Y06 |  |
| 7 | EXD108/20 | CR1-X07 CR1-X08 |  | 18 | (EXD119/20) | --- | unused |
| 8 | EXD109/20 | CR1-Y11 CR1-Y12 |  | 19 | (EXD120/20) | --- | unused |
| 9 | EXD110/20 | CR1-X09 CR1-X10 |  | 20 | (EXD121/20) | --- | unused |
| 10 | EXD111/20 | CR1-X11 |  | 21 | (EXD122/20) | --- | unused |
| 11 | (EXD112/20) | --- | unused | 22 | EXD123/20 | CR1-Z09 CR1-Z10 |  |

EXD2/20 in CR2 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD202/20 | CR2-X01* CR2-X02 |  | 12 | EXD213/20 | CR2-Y13 CR2-Y14 |  |
| 2 | EXD203/20 | CR2-X03 CR2-X04 |  | 13 | EXD214/20 | CR2-Y15 CR2-Y16 |  |
| 3 | EXD204/20 | CR2-X05 CR2-X06 |  | 14 | EXD215/20 | CR2-Y17 |  |
| 4 | EXD205/20 | CR2-X07 CR2-X08 |  | 15 | EXD216/20 | CR2-Z01 CR2-Z02 |  |
| 5 | EXD206/20 | CR2-X09 CR2-X10 |  | 16 | EXD217/20 | CR2-Z03 CR2-Z04 |  |
| 6 | (EXD207/20) | --- | unused | 17 | EXD218/20 | CR2-Z05 CR2-Z06 |  |
| 7 | (EXD208/20) | --- | unused | 18 | EXD219/20 | CR2-Z07 CR2-Z08 |  |
| 8 | EXD209/20 | CR2-Y05 CR2-Y06 |  | 19 | EXD220/20 | CR2-Z09 CR2-Z10 |  |
| 9 | EXD210/20 | CR2-Y07 CR2-Y08 |  | 20 | EXD221/20 | CR2-Z11 CR2-Z12 |  |
| 10 | EXD211/20 | CR2-Y09 CR2-Y10 |  | 21 | EXD222/20 | CR2-Z13 |  |
| 11 | EXD212/20 | CR2-Y11 CR2-Y12 |  | 22 | (EXD223/20) | --- | unused |

EXD3/20 in CR3 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD302/20 | CR3-X05 CR3-X06 |  | 12 | EXD313/20 | CR3-Y09 CR3-Y10 | SRC SRC |
| 2 | EXD303/20 | CR3-X03 CR3-X04 |  | 13 | (EXD314/20) | --- | unused |
| 3 | EXD304/20 | CR3-X07 CR3-X08 |  | 14 | (EXD315/20) | --- | unused |
| 4 | EXD305/20 | CR3-X01 CR3-X02 |  | 15 | (EXD316/20) | --- | unused |
| 5 | EXD306/20 | CR3-X09 CR3-X10 |  | 16 | (EXD317/20) | --- | unused |
| 6 | (EXD307/20) | --- | unused | 17 | (EXD318/20) | --- | unused |
| 7 | EXD308/20 | CR3-Y03 CR3-Y04 |  | 18 | (EXD319/20) | --- | unused |
| 8 | EXD309/20 | CR3-Y13 | SRC | 19 | EXD320/20 | CR3-Z09 CR3-Z10 | SRC SRC |
| 9 | EXD310/20 | CR3-Y05 CR3-Y06 | SRM SRM | 20 | EXD321/20 | CR3-X11 CR3-X12 |  |
| 10 | EXD311/20 | CR3-Y11 CR3-Y12 | SRC SRC | 21 | (EXD322/20) | --- | unused |
| 11 | EXD312/20 | CR3-Y07 CR3-Y08 | SRM SRM | 22 | EXD323/20 | CR3-Y01* CR3-Y02 |  |

EXD4/20 in CR4 (Haz-D)

| # | HM # | Rack | Spare Status | # | HM # | Rack | Spare Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | EXD402/20 | CR4-X06 CR4-X07 | SRM | 12 | EXD413/20 | CR4-Y12 CR4-Y13 |  |
| 2 | EXD403/20 | CR4-Z01* |  | 13 | EXD414/20 | CR4-Y10 CR4-Y11 |  |
| 3 | EXD404//20 | CR4-Z02 CR4-Z03 |  | 14 | EXD415/20 | CR4-X04 CR4-X05 |  |
| 4 | EXD405/20 | CR4-Z04 CR4-Z05 |  | 15 | EXD416/20 | CR4-X08 CR4-X09 | SRM SRM |
| 5 | EXD406/20 | CR4-Z06 CR4-Z07 | SRM | 16 | EXD417/20 | CR4-Y08 CR4-Y09 | SRM |
| 6 | EXD407/20 | CR4-Y01 CR4-Y02 |  | 17 | (EXD418/20) | --- | unused |
| 7 | EXD408/20 | CR4-Y03 |  | 18 | EXD419/20 | CR4-X03 |  |
| 8 | EXD409/20 | CR4-Y04 CR4-Y05 |  | 19 | (EXD420/20) | --- | unused |
| 9 | EXD410/20 | CR4-X10 CR4-X11 | SRC SRC | 20 | EXD421/20 | CR4-X01 CR4-X02 |  |
| 10 | EXD411/20 | CR4-Y14 | SRM | 21 | (EXD422/20) | --- | unused |
| 11 | EXD412/20 | CR4-Y06 CR4-Y07 | SRM | 22 | (EXD423/20) | --- | unused |

EXD5/20 in CR5 (Haz-S)

| # | HM # | Rack | Spare Status |
| --- | --- | --- | --- |
| 1 | (EXD502/20) | --- | unused |
| 2 | (EXD503/20) | --- | unused |
| 3 | (EXD504/20) | --- | unused |
| 4 | (EXD505/20) | --- | unused |
| 5 | (EXD506/20) | --- | unused |
| 6 | (EXD507/20) | --- | unused |
| 7 | EXD508/20 | CR5-X07 CR5-X08 |  |
| 8 | (EXD509/20) | --- | unused |
| 9 | (EXD510/20) | --- | unused |

EBD8/2X in SX2 (‘Prisma’ wall switchboard near PX24 access point)

| # | Name |  | Rack (ACR) | Spare Status |
| --- | --- | --- | --- | --- |
| 1 | EBD802/2X |  | SX2-X02 |  |
| 2 | (EBD803/2X) |  | --- | unused |
| 3 | (EBD804/2X) |  | --- | unused |
| 4 | (EBD805/2X) |  | --- | unused |
| 5 | (EBD806/2X) |  | --- | unused |
| 6 | (EBD807/2X) |  | --- | unused |
| 7 | (EBD808/2X) |  | --- | unused |
| 8 | (EBD809/2X) | --- |  | unused |
| 9 | (EBD810/2X) |  | --- | unused |

## Appendix C: Distribution of Power to Cooling Units

TS-CV1 Standard Power Distribution

(FCTIR-024)

| Feeder # | Cooling Unit | Power Consumption (kW) |
| --- | --- | --- |
| 1 | SPD | 3 |
| 2 | SDD+SSD | 35 |
| 3 | TPC | 115 |
| 4 | TRD+Screen | 70 |
| 5 | TOF+PHOS electronics | 12 |
| 6 | HMPID | 4 |
| 7 | PHOS crystals | 27 |
| 8 | Bus Bars | 4 |
| 9 | unused |  |
| Total |  | 270 |

TS-CV2 UPS-level 2 Power Distribution

(FCTIR-025)

| Feeder # | Cooling Unit | Power Consumption (W) |
| --- | --- | --- |
| 1 | SPD | 850 |
| 2 | SDD+SSD | 680 |
| 3 | TPC | 920 |
| 4 | TRD+Screen | 680 |
| 5 | TOF+PHOS electronics | 680 |
| 6 | HMPID | 440 |
| 7 | PHOS crystals | 1500 |
| 8 | Bus Bars | 600 |
| 9 | unused |  |
| Total |  | 6350 |

## Appendix D: Distribution of UPS power in ALICE

UPS1 (20 kVA)

via EOD3/2X  in SX2 (‘Prisma’ wall switchboard)

| # | Departure # | Rack | Function | Spare Status |
| --- | --- | --- | --- | --- |
| 1 | (EOD302/2X) | --- | --- | unused |
| 2 | EOD303/2X | 1 rack in MCR | MSS |  |
| 2 | EOD303/2X | 1 rack in MCR | MSS |  |
| 3 | EOD304/2X | CR4-Z09 | DCS-DSS |  |
| 4 | EOD305/2X | SX2-X01 | DCS-DSS (ACR) |  |
| 5 | (EOD306/2X) | --- | --- | unused |
| 6 | EOD307/2X | O23 | Sniffer Spare |  |
| 6 | EOD307/2X | O22 | Sniffer Detection |  |
| 6 | EOD307/2X | O21 | Sniffer Detection |  |
| 7 | (EOD308/2X) | --- | --- | unused |
| 8 | (EOD309/2X) | --- | --- | unused |
| 9 | EOD310/2X | CR4-Z08 | TPC-VHV |  |

UPS2 (80 kVA)

via EOD1/20 in CR4 (Haz-D)

| # | HM # | Rack | Function | Spare Status |
| --- | --- | --- | --- | --- |
| 1 | EOD102/20 | CR3-Z01 | DCS |  |
| 2 | EOD103/20 | CR3-Z02 | DCS |  |
| 3 | EOD104/20 | CR3-Z03 | DCS |  |
| 4 | EOD105/20 | CR3-Z04 | DCS |  |
| 5 | EOD106/20 | CR3-Z05 | DCS |  |
| 6 | EOD107/20 | CR3-Z06 | DCS |  |
| 7 | EOD108/20 | CR3-Z07 | DCS |  |
| 8 | EOD109/20 | CR3-Z08 | DCS |  |
| 9 | EOD110/20 | CR2-Y01 | HLT |  |
| 10 | EOD111/20 | CR2-Y02 | HLT |  |
| 11 | EOD112/20 | CR2-Y03 | HLT |  |
| 12 | EOD113/20 | CR2-Y04 | HLT |  |
| 13 | (EOD114/20) | --- | --- | unused |
| 14 | (EOD115/20) | --- | --- | unused |
| 15 | (EOD116/20) | --- | --- | unused |
| 16 | (EOD117/20) | --- | --- | unused |
| 17 | (EOD118/20) | --- | --- | unused |
| 18 | (EOD119/20) | --- | --- | unused |
| 19 | (EOD120/20) | --- | --- | unused |
| 20 | (EOD121/20) | --- | --- | unused |
| 21 | (EOD122/20) | --- | --- | unused |
| 22 | (EOD123/20) | --- | --- | unused |

UPS3 (60 kVA)

via EOD1/2X in SX2 (Haz-S)

| # | HM # | Rack | Function | Spare Status |
| --- | --- | --- | --- | --- |
| 1 | EOD102/2X | CR1-Z02 | DAQ |  |
| 1 | EOD102/2X | CR1-Z03 | DAQ |  |
| 1 | EOD102/2X | CR1-Z04 | DAQ |  |
| 2 | EOD103/2X | CR1-Z05 | DAQ |  |
| 2 | EOD103/2X | CR1-Z06 | DAQ |  |
| 2 | EOD103/2X | CR1-Z07 | DAQ |  |
| 2 | EOD103/2X | CR1-Z08 | DAQ |  |
| 3 | (EOD104/2X) | --- | --- | unused |
| 4 | EOD105/2X | CR5-X01 | Sniffer Control |  |
| 4 | EOD105/2X | CR5-X02 | Fire Detection (racks) |  |
| 4 | EOD105/2X | CR5-X03 | Fire Detection (racks) |  |
| 4 | EOD105/2X | CR5-X04 | Fire Detection (cavern) |  |
| 4 | EOD105/2X | CR5-X05 | Radio- protection |  |
| 4 | EOD105/2X | CR5-X06 | Safety Spare |  |
| 5 | (EOD106/2X) | --- | --- | unused |
| 6 | (EOD107/2X) | --- | --- | unused |
| 7 | EOD108/2X | TS-CV2 | Cooling Units in C |  |
| 8 | (EOD109/2X) | --- | --- | unused |
| 9 | (EOD110/2X) | --- | --- | unused |

Refer to EDMS documents ALI-SER-SPC-0021 and ALI-SER-SPC-0022 for the definition (location and allocation) of electronic racks in ALICE

Hazemeyer Module (HM): a set of 3-phase circuit breaker/contactor with remote control

racks installed only (spares not included)